## Sheet1
Specific Heat of Water	4.1813	KJ/L/C	71654.94	BTU/HR
System Heat Load	21000	Watts	75600	KJ/H
Water In Temp ©	20	Cooling water inlet temperature
Water Out Temp ©	30	Cooling water discharge temperature
Sink Capacity of 1L / S	41.813	K/J
Flow required	0.5022361467	L/S	Cooling water flow in Litres/S
	30.1341687992	L/M	7.9606052262	GPM
	1808.0501279506	L/H

Gas In ©	39	Compressor Discharge Temperature In Celcius
Liquid Out ©	26	Condensed Liquid with 0 Subcooling
LMTD	17.0366207618
U (W/M2/C)	150	HX Transfer Coefficient
W/M2	2555.4931142704
Area M2	8.2175920893

Only alter numbers highlighted in BLUE
Use a U value ~ 150 for a Condenser, ~800 for an Evaporator, ~1500 Water to Water